## DOMESTIC DEMAND
RESIDENTIAL METER SIZING WORKSHEET ONLY
(REFERENCE UPC 2012 APPENDIX A, TABLE 2.1 AND APPENDIX C, TABLE C 4.1, WSFU, Flush Tanks)
Project Name:
LVVWD Project Number:
Calculations herein are for floor plan/model:
GROUPED FIXTURES
BATHROOM GROUPS1 AND 2 | FIXTURE UNITS COLD | QUANTITIES | TOTAL
CLICK HERE TO SELECT A BATHROOM GROUP: | 0 | 1 | 0
AND Each Additional 1/2 Bath | 0.5 |  | 0
AND Each Additional Bathroom Group | 1 |  | 0
AND Each Bidet | 1 |  | 0
AND Each Shower (if Bath has separate tub & shower) | 2 |  | 0
Kitchen Group (Sink and Dishwasher) 3 | 2 |  | 0
Laundry Group (Sink and Clothes Washer) 3 | 5 |  | 0
ADDITIONAL FIXTURES NOT GROUPED
Wet Bar/Bar Sink | 1 |  | 0
Kitchen Sink | 1.5 |  | 0
Laundry Sink | 1.5 |  | 0
Service/Mop Sink | 1.5 |  | 0
Diswasher | 1.5 |  | 0
Urinal | 2 |  | 0
Clothes Washer | 4 |  | 0
Hose Bibb | 2.5 |  | 0
Each Additional Hose Bibb | 1 |  | 0
TOTAL FIXTURE UNITS |  |  | 0
DOMESTIC DEMAND (FIXTURE UNITS TO GPM CONVERSION) |  |  | 0
METER SIZE4 |  |  | 3/4 inch
NOTES:
1. Bathroom Groups having 1.6 GPF Gravity-Tank Water Closets. One bathroom group, for the purposes of this worksheet, consists of one water closet, up to two lavatories, and either one bathtub or one shower.
2. A half-bath or powder room, for the pursoses of this worksheet, consists of one water closet and one lavatory.
3. The District will only account for one Kitchen and Laundry Group for a Single Family. Additional Kichenettes and Stackable washers will be accounted for separately as non-grouped fixtures.
4. LVVWD requires a minimum 3/4" meter for Domestic Services. This tool calculates the domestic demand at 70% of the maximum flow for each meter capacity, allowing the rest for irrigation.
5. If Residential Fire Sprinklers are required to be served by the domestic meter, the maximum allowable flow of the meter will be allowed for a fire event only.

## VALUES2 (hidden)
FLOW (GPM) | FIXTURE UNITS (Flush Tank)
0 | 0 | 0
1 | 0.5 | 0 | CLICK HERE TO SELECT A BATHROOM GROUP: | 0
2 | 1 | 0 | Half Bath or Powder Room | 3.5
2.25 | 1.5 | 0 | 1 Bathroom Group | 5
2.5 | 2 | 0 | 1-1/2 Bathrooms | 6
2.75 | 2.5 | 0 | 2 Bathrooms | 7
3 | 3 | 0 | 2-1/2 Bathrooms | 8
3.5 | 3.5 | 0 | 3 Bathrooms | 9
4 | 4 | 0
4.25 | 4.5 | 0
4.5 | 5 | 0
4.75 | 5.5 | 0
5 | 6 | 0
5.5 | 6.5 | 0
6 | 7 | 0
6.5 | 7.5 | 0
7 | 8 | 0
7.25 | 8.5 | 0
7.5 | 9 | 0
7.75 | 9.5 | 0
8 | 10 | 0
8.25 | 10.5 | 0
8.5 | 11 | 0
8.75 | 11.5 | 0
9 | 12 | 0
9.5 | 12.5 | 0
10 | 13 | 0
10.25 | 13.5 | 0
10.5 | 14 | 0
10.75 | 14.5 | 0
11 | 15 | 0
11.5 | 15.5 | 0
12 | 16 | 0
12.25 | 16.5 | 0
12.5 | 17 | 0
12.75 | 17.5 | 0
13 | 18 | 0
13.25 | 18.5 | 0
13.5 | 19 | 0
13.75 | 19.5 | 0
14 | 20 | 0
14.5 | 20.5 | 0
15 | 21 | 0
15.25 | 21.5 | 0
15.5 | 22 | 0
15.75 | 22.5 | 0
16 | 23 | 0
16.5 | 23.5 | 0
17 | 24 | 0
17.25 | 24.5 | 0
17.5 | 25 | 0
17.75 | 25.5 | 0
18 | 26 | 0
18.25 | 26.5 | 0
18.5 | 27 | 0
18.75 | 27.5 | 0
19 | 28 | 0
19.25 | 28.5 | 0
19.5 | 29 | 0
19.75 | 29.5 | 0
20 | 30 | 0
20.25 | 30.5 | 0
20.5 | 31 | 0
20.75 | 31.5 | 0
21 | 32 | 0
21.25 | 32.5 | 0
21.5 | 33 | 0
21.75 | 33.5 | 0
22 | 34 | 0
22.25 | 34.5 | 0
22.5 | 35 | 0
22.75 | 35.5 | 0
23 | 36 | 0
23.1667 | 36.5 | 0
23.3333 | 37 | 0
23.5 | 37.5 | 0
23.6667 | 38 | 0
23.8333 | 38.5 | 0
24 | 39 | 0
24.1667 | 39.5 | 0
24.3333 | 40 | 0
24.5 | 40.5 | 0
24.6667 | 41 | 0
24.8333 | 41.5 | 0
25 | 42 | 0
25.25 | 42.5 | 0
25.5 | 43 | 0
25.75 | 43.5 | 0
26 | 44 | 0
26.25 | 44.5 | 0
26.5 | 45 | 0
26.75 | 45.5 | 0
27 | 46 | 0
27.1667 | 46.5 | 0
27.3333 | 47 | 0
27.5 | 47.5 | 0
27.6667 | 48 | 0
27.8333 | 48.5 | 0
28 | 49 | 0
28.25 | 49.5 | 0
28.5 | 50 | 0
28.75 | 50.5 | 0
29 | 51 | 0
29.1667 | 51.5 | 0
29.3333 | 52 | 0
29.5 | 52.5 | 0
29.6667 | 53 | 0
29.8333 | 53.5 | 0
30 | 54 | 0
30.25 | 54.5 | 0
30.5 | 55 | 0
30.75 | 55.5 | 0
31 | 56 | 0
31.25 | 56.5 | 0
31.5 | 57 | 0
31.75 | 57.5 | 0
32 | 58 | 0
32.25 | 58.5 | 0
32.5 | 59 | 0
32.75 | 59.5 | 0
33 | 60 | 0
33.1667 | 60.5 | 0
33.3333 | 61 | 0
33.5 | 61.5 | 0
33.6667 | 62 | 0
33.8333 | 62.5 | 0
34 | 63 | 0
34.1667 | 63.5 | 0
34.3333 | 64 | 0
34.5 | 64.5 | 0
34.6667 | 65 | 0
34.8333 | 65.5 | 0
35 | 66 | 0
35.1667 | 66.5 | 0
35.3333 | 67 | 0
35.5 | 67.5 | 0
35.6667 | 68 | 0
35.8333 | 68.5 | 0
36 | 69 | 0
36.1 | 69.5 | 0
36.2 | 70 | 0
36.3 | 70.5 | 0
36.4 | 71 | 0
36.5 | 71.5 | 0
36.6 | 72 | 0
36.7 | 72.5 | 0
36.8 | 73 | 0
36.9 | 73.5 | 0
37 | 74 | 0
37.125 | 74.5 | 0
37.25 | 75 | 0
37.375 | 75.5 | 0
37.5 | 76 | 0
37.625 | 76.5 | 0
37.75 | 77 | 0
37.875 | 77.5 | 0
38 | 78 | 0
38.1 | 78.5 | 0
38.2 | 79 | 0
38.3 | 79.5 | 0
38.4 | 80 | 0
38.5 | 80.5 | 0
38.6 | 81 | 0
38.7 | 81.5 | 0
38.8 | 82 | 0
38.9 | 82.5 | 0
39 | 83 | 0
39.1667 | 83.5 | 0
39.3333 | 84 | 0
39.5 | 84.5 | 0
39.6667 | 85 | 0
39.8333 | 85.5 | 0
40 | 86 | 0
40.125 | 86.5 | 0
40.25 | 87 | 0
40.375 | 87.5 | 0
40.5 | 88 | 0
40.625 | 88.5 | 0
40.75 | 89 | 0
40.875 | 89.5 | 0
41 | 90 | 0
41.1 | 90.5 | 0
41.2 | 91 | 0
41.3 | 91.5 | 0
41.4 | 92 | 0
41.5 | 92.5 | 0
41.6 | 93 | 0
41.7 | 93.5 | 0
41.8 | 94 | 0
41.9 | 94.5 | 0
42 | 95 | 0
42.125 | 95.5 | 0
42.25 | 96 | 0
42.375 | 96.5 | 0
42.5 | 97 | 0
42.625 | 97.5 | 0
42.75 | 98 | 0
42.875 | 98.5 | 0
43 | 99 | 0
43.125 | 99.5 | 0
43.25 | 100 | 0
43.375 | 100.5 | 0
43.5 | 101 | 0
43.625 | 101.5 | 0
43.75 | 102 | 0
43.875 | 102.5 | 0
44 | 103 | 0
44.125 | 103.5 | 0
44.25 | 104 | 0
44.375 | 104.5 | 0
44.5 | 105 | 0
44.625 | 105.5 | 0
44.75 | 106 | 0
44.875 | 106.5 | 0
45 | 107 | 0
45.125 | 107.5 | 0
45.25 | 108 | 0
45.375 | 108.5 | 0
45.5 | 109 | 0
45.625 | 109.5 | 0
45.75 | 110 | 0
45.875 | 110.5 | 0
46 | 111 | 0
46.125 | 111.5 | 0
46.25 | 112 | 0
46.375 | 112.5 | 0
46.5 | 113 | 0
46.625 | 113.5 | 0
46.75 | 114 | 0
46.875 | 114.5 | 0
47 | 115 | 0
47.125 | 115.5 | 0
47.25 | 116 | 0
47.375 | 116.5 | 0
47.5 | 117 | 0
47.625 | 117.5 | 0
47.75 | 118 | 0
47.875 | 118.5 | 0
48 | 119 | 0
48.125 | 119.5 | 0
48.25 | 120 | 0
48.375 | 120.5 | 0
48.5 | 121 | 0
48.625 | 121.5 | 0
48.75 | 122 | 0
48.875 | 122.5 | 0
49 | 123 | 0
49.125 | 123.5 | 0
49.25 | 124 | 0
49.375 | 124.5 | 0
49.5 | 125 | 0
49.625 | 125.5 | 0
49.75 | 126 | 0
49.875 | 126.5 | 0
50 | 127 | 0
50.2326 | 128 | 0
50.4651 | 129 | 0
50.6977 | 130 | 0
50.9302 | 131 | 0
51.1628 | 132 | 0
51.3953 | 133 | 0
51.6279 | 134 | 0
51.8605 | 135 | 0
52.093 | 136 | 0
52.3256 | 137 | 0
52.5581 | 138 | 0
52.7907 | 139 | 0
53.0233 | 140 | 0
53.2558 | 141 | 0
53.4884 | 142 | 0
53.7209 | 143 | 0
53.9535 | 144 | 0
54.186 | 145 | 0
54.4186 | 146 | 0
54.6512 | 147 | 0
54.8837 | 148 | 0
55.1163 | 149 | 0
55.3488 | 150 | 0
55.5814 | 151 | 0
55.814 | 152 | 0
56.0465 | 153 | 0
56.2791 | 154 | 0
56.5116 | 155 | 0
56.7442 | 156 | 0
56.9767 | 157 | 0
57.2093 | 158 | 0
57.4419 | 159 | 0
57.6744 | 160 | 0
57.907 | 161 | 0
58.1395 | 162 | 0
58.3721 | 163 | 0
58.6047 | 164 | 0
58.8372 | 165 | 0
59.0698 | 166 | 0
59.3023 | 167 | 0
59.5349 | 168 | 0
59.7674 | 169 | 0
60 | 170 | 0
60.2 | 171 | 0
60.4 | 172 | 0
60.6 | 173 | 0
60.8 | 174 | 0
61 | 175 | 0
61.2 | 176 | 0
61.4 | 177 | 0
61.6 | 178 | 0
61.8 | 179 | 0
60 | 180 | 0
60.25 | 181 | 0
60.5 | 182 | 0
60.75 | 183 | 0
61 | 184 | 0
61.25 | 185 | 0
61.5 | 186 | 0
61.75 | 187 | 0
62 | 188 | 0
62.25 | 189 | 0
62.5 | 190 | 0
62.75 | 191 | 0
63 | 192 | 0
63.25 | 193 | 0
63.5 | 194 | 0
63.75 | 195 | 0
64 | 196 | 0
64.25 | 197 | 0
64.5 | 198 | 0
64.75 | 199 | 0
65 | 200 | 0
65.1 | 201 | 0
65.2 | 202 | 0
65.3 | 203 | 0
65.4 | 204 | 0
65.5 | 205 | 0
65.6 | 206 | 0
65.7 | 207 | 0
65.8 | 208 | 0
65.9 | 209 | 0
66 | 210 | 0
66.1 | 211 | 0
66.2 | 212 | 0
66.3 | 213 | 0
66.4 | 214 | 0
66.5 | 215 | 0
66.6 | 216 | 0
66.7 | 217 | 0
66.8 | 218 | 0
66.9 | 219 | 0
67 | 220 | 0
67.2 | 221 | 0
67.4 | 222 | 0
67.6 | 223 | 0
67.8 | 224 | 0
68 | 225 | 0
68.2 | 226 | 0
68.4 | 227 | 0
68.6 | 228 | 0
68.8 | 229 | 0
69 | 230 | 0
69.2 | 231 | 0
69.4 | 232 | 0
69.6 | 233 | 0
69.8 | 234 | 0
70 | 235 | 0
70.2 | 236 | 0
70.4 | 237 | 0
70.6 | 238 | 0
70.8 | 239 | 0
71 | 240 | 0
71.2 | 241 | 0
71.4 | 242 | 0
71.6 | 243 | 0
71.8 | 244 | 0
72 | 245 | 0
72.2 | 246 | 0
72.4 | 247 | 0
72.6 | 248 | 0
72.8 | 249 | 0
73 | 250 | 0